## PANIC-S2I
tag | description | severity | receivers | system | podsystem | Opis funkcyjny alarmu: | device | formula | sms | Logbook: | update | Komentarz:
R1_MAG_CIRCUIT_RES_1 | Dangerous change of circuit resistance - PS1 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,56 * 1,1 ) < Resistance [ R1-C134-MAG-PS1 ] < ( 0,56 * 0,9 )) and ( t > 10 s ) ) | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Nie | Tak
R1_MAG_CIRCUIT_RES_1_WAR | Dangerous change of circuit resistance - PS1 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,56 * 1,05 ) < Resistance [ R1-C134-MAG-PS1 ] < ( 0,56 * 0,95 )) and ( t > 10 s ) ) | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Nie | Tak
R1_C134_PS1_INTERLOCK | Interlock inside Danfysik PS1 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-C134-MAG-PS1 power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside Danfysik PS1
R1_C134_PS1_WaterFlow | Cooling water flow is too low for PS1 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | External flow switch trigger in C134 for PS1 (HVAC) | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Cooling water flow is below 10L/min value or mechanical failure or signal lost
R1_C134_PS2_INTERLOCK | Interlock inside Danfysik PS2 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-C134-MAG-PS2 power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside Danfysik PS2
R1_C134_PS2_WaterFlow | Cooling water flow is too low for PS2 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | External flow switch trigger in C134 for PS2 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Cooling water flow is below 10L/min value
R1_C134_PS3_INTERLOCK | Interlock inside Danfysik PS3 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-C134-MAG-PS3 power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside Danfysik PS3
R1_C134_PS3_WaterFlow | Cooling water flow is too low for PS3 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | External flow switch trigger in C134 for PS3 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Cooling water flow is below 18L/min value
R1_C134_PS4_INTERLOCK | Interlock inside Danfysik PS4 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-C134-MAG-PS4 power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside Danfysik PS4
R1_C134_PS4_WaterFlow | Cooling water flow is too low for PS4 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | External flow switch trigger in C134 for PS4 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Cooling water flow is below 10L/min value
R1_C134_PS5_INTERLOCK | Interlock inside Danfysik PS5 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-C134-MAG-PS5 power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside Danfysik PS5
R1_C134_PS5_WaterFlow | Cooling water flow is too low for PS5 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | External flow switch trigger in C134 for PS5 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Cooling water flow is below 13L/min value
R1_C134_PS19_SI_INTERLOCK | Interlock inside SI 19 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside R1-SGBCAB06-MAG-PS19 (SI) power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Interlock inside SI PS
R1_SGB_PS19_SI | Inner temperature is higher than 58C deg | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Temp > 58 C deg, R1-SGBCAB06-MAG-PS19 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Inner temperature is higher than 58C deg
R1_SGB_PS19_SI_TEMP_WAR | Inner temperature is higher than 54C deg | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Temp > 54 C deg, R1-SGBCAB06-MAG-PS19 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Inner temperature is higher than 54C deg
R1_SGA_PSH1 | Inner interlock | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Any interlock inside power supply
R1_SGA_PSH1_CURRENT | Current warning | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | If current < 0,001 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | PS current is too low
R1_SGA_PSV1 | Inner interlock | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | Any interlock inside power supply | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Any interlock inside power supply
R1_SGA_PSV1_CURRENT | Current warning | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | If current < 0,001 | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | PS current is too low
R1_SGDCAB12_MAG_PS01 | Interlock inside PS for TL | INFO | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( BSs open and ( any interlock inside power supply ) ) | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Any interlock inside power supply
R1_SGDCAB12_MAG_PS02 | Interlock inside PS for TL | INFO | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( BSs open and ( any interlock inside power supply ) ) | ALARM/MAG/R1_MAG_PYALARM02 | False | +48 519 307 974 | Tak | Tak | Any interlock inside power supply
I_VAC_GUN_SIP | Gun pressure problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if ((1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU1/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU2/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU3/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU4/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU5/Pressure < 1e-9 )) and ( t < 1800 s ) ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | Gun decay pressure too long
I_VAC_EF_SIP | Energy fiter pressure problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if ((1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU6/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU7/Pressure < 1e-9 )) and ( t < 1800 s ) ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | Energy filter decay pressure too long
I_K00_VAC_SCRN1 | Linac YAG-Screen SCRN1 pressure problem in K00 | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-SOO/DIA/I-SOO-DIA-SCRN1 == 0) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU6/Pressure < 1e-9 ) and (1e-7 < I-K00/VAC/I-K00CAB01-VAC-IPCU7/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN1 in K00 is causing problem
I_K01_VAC_SCRN1 | Linac YAG-Screen SCRN1 pressure problem in K01 | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-SO1A/DIA/I-SO1A-DIA-SCRN1 == 0) and (1e-7 < I-K01/VAC/I-K01CAB05-VAC-IPCU1/Pressure < 1e-9 ) and (1e-7 < I-K01/VAC/I-K01CAB05-VAC-IPCU2/Pressure < 1e-9 ) and (1e-7 < I-K01/VAC/I-K01CAB05-VAC-IPCU3/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN1 in K01 is causing problem
I_K02_VAC_SCRN1 | Linac YAG-Screen SCRN1 pressure problem in K02 | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-SO2B/DIA/I-SO2B-DIA-SCRN1 == 0) and (1e-7 < I-K02/VAC/I-K02CAB05-VAC-IPCU4/Pressure < 1e-9 ) and (1e-7 < I-K02/VAC/I-K02CAB05-VAC-IPCU5/Pressure < 1e-9 ) and (1e-7 < I-K02/VAC/I-K02CAB05-VAC-IPCU6/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN1 in K02 is causing problem
I_K03_VAC_SCRN1 | Linac YAG-Screen SCRN1 pressure problem in K03 | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-SO3B/DIA/I-SO3B-DIA-SCRN1 == 0) and (1e-7 < I-K03/VAC/I-K03CAB05-VAC-IPCU1/Pressure < 1e-9 ) and (1e-7 < I-K03/VAC/I-K03CAB05-VAC-IPCU2/Pressure < 1e-9 ) and (1e-7 < I-K03/VAC/I-K03CAB05-VAC-IPCU3/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN1 in K03 is causing problem
I_TL_VAC_SCRN1 | TL YAG-Screen SCRN1 pressure problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-TR1/DIA/I-TR1-DIA-SCRN1 == 0) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU1/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN1 in TL is causing problem
I_TL_VAC_SCRN2 | TL YAG-Screen SCRN2 pressure problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-TR1/DIA/I-TR1-DIA-SCRN2 == 0) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU2/Pressure < 1e-9 ) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU3/Pressure < 1e-9 ) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU4/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN2 in TL is causing problem
I_TL_VAC_SCRN3 | TL YAG-Screen SCRN1 pressure problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | I | VAC | if (I-TR1/DIA/I-TR1-DIA-SCRN2 == 0) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU4/Pressure < 1e-9 ) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU5/Pressure < 1e-9 ) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU6 /Pressure < 1e-9 ) and (1e-7 < I-TL/VAC/I-TLCAB02-VAC-IPCU7/Pressure < 1e-9 )) and ( t < 1800 s ) | ALARM/VAC/I_VAC_PYALARM01 | False | +48 571 445 044 | Tak | Tak | YAG-Screen SCRN3 in TL is causing problem
R1_01S_VAC_VALVE | Ring valve open problem | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | R1 | VAC | if (R1-01S/VAC/R1-01S-VAC-VGRC1 / valveOpen == False and R1-01S/VAC/R1-01S-VAC-VGRC2/valveOpen == False and R1-ALL/CTL/R1-ALL-CTL-STMA1/MachineState==BeamFB) and (t < 300 s) | ALARM/VAC/R1_VAC_PYALARM02 | False | +48 571 445 044 | Tak | Tak | In case not possibility to open valve
FE_05ID_VAC_OPEN | One of absorber, shutter, valve on the front end stayed closed | INFO | Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | R1 | VAC | if(r1-05feid/vac/r1-05feid-vac-vgfa1/ValveOpen == False and r1-05/vac/r1-05-vac-abs1InExStatus == True) and (t < 300 s) | ALARM/VAC/R1_VAC_PYALARM02 | False | +48 571 445 044 | Tak | Tak | Front end stayed closed, problem with light delivery
R1_CTL_PS_RST | Power Supply reset done by state machine | INFO | Wojciech Kitka, wojciech.kitka@uj.edu.pl | R1 | CTL | if R1-ALL/CTL/R1-ALL-CTL-STMA1/PowerSuppliesReset == True | ALARM/CTL/R1_CTL_PYALARM02 | False | +48 504 778 793 | Nie | Tak | Problem can occure after beam lost
R1_CTL_BEAM_LOST | Beam lost | WARNING | Wojciech Kitka, wojciech.kitka@uj.edu.pl | R1 | CTL | if R1-ALL/CTL/R1-ALL-CTL-STMA1/MachineState == BeamLost | ALARM/CTL/R1_CTL_PYALARM02 | False | +48 504 778 793 | Nie | Tak | Random source of problem
R1_CTL_BEAM_DUMP | Beam dump | INFO | Wojciech Kitka, wojciech.kitka@uj.edu.pl | R1 | CTL | if R1-ALL/CTL/R1-ALL-CTL-STMA1/MachineState == BeamDump | ALARM/CTL/R1_CTL_PYALARM02 | False | +48 504 778 793 | Nie | Tak | Beam was dumped by Operator
RAD_BRM_WARNING | Any Radiation Station exceeded Gamma Dose Rate or Total Dose rate-- Alarm 2 | INFO | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(((BL-02ID-PSS-BRM1.Gamma Dose Rate or BL-02ID-PSS-BRM1.Total Dose Rate) > BL-02ID-PSS-BRM1.AlarmLimitDoseRate2)or(BL-04BM-PSS-BRM1.Gamma Dose Rate or BL-04BM-PSS-BRM1.Total Dose Rate > BL-04BM-PSS-BRM1.AlarmLimitDoseRate2 )or (BL-05ID-PSS-BRM1.Gamma Dose Rate or BL-05ID-PSS-BRM1.Total Dose Rate) > BL-05ID-PSS-BRM1.AlarmLimitDoseRate2 )or(( BL-06ID-PSS-BRM1.Gamma Dose Rate or BL-06ID-PSS-BRM1.Total Dose Rate) > BL-06ID-PSS-BRM1.AlarmLimitDoseRate2)or( R1-01R-PSS-BRM1.Gamma Dose Rate or R1-01R-PSS-BRM1.Total Dose Rate) > R1-01R-PSS-BRM1.AlarmLimitDoseRate2 )or(BL-01-PSS-BRM1.Gamma Dose Rate or BL-01-PSS-BRM1.Total Dose Rate) > BL-01-PSS-BRM1.AlarmLimitDoseRate2 )or(R1-SGA-PSS-BRM1.Gamma Dose Rate or R1-SGA-PSS-BRM1.Total Dose Rate) > R1-SGA-PSS-BRM1.AlarmLimitDoseRate2 )or (BL-02BM-PSS-BRM1.Gamma Dose Rate or BL-02BM-PSS-BRM1.Total Dose Rate) > BL-02BM-PSS-BRM1.AlarmLimitDoseRate2 )or(BL-08ID-PSS-BRM1.Gamma Dose Rate or BL-08ID-PSS-BRM1.Total Dose Rate) > BL-08ID-PSS-BRM1.AlarmLimitDoseRate2 ))) and R1-ALL/CTL/R1-ALL-CTL-STMA1/MachineState == BeamFB | ALARM/RAD/R1_RAD_PYALARM02 | False | +48 571 240 691 | Nie | Tak | in case of radiation leak, e.g. beam lost, beam dump
RAD_BRM_ALARM | Any Radiation Station exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if((BL-02ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-02ID-PSS-BRM1.AlarmLimitShiftDose2)or(BL-04BM-PSS-BRM1.AccumulatedTotalShiftDose > BL-04BM-PSS-BRM1.AlarmLimitShiftDose2)or(BL-05ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-05ID-PSS-BRM1.AlarmLimitShiftDose2)or((BL-06ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-06ID-PSS-BRM1.AlarmLimitShiftDose2)or(R1-01R-PSS-BRM1.AccumulatedTotalShiftDose > R1-01R-PSS-BRM1.AlarmLimitShiftDose2 )or(BL-01-PSS-BRM1.AccumulatedTotalShiftDose > BL-01-PSS-BRM1.AlarmLimitShiftDose2)or( R1-SGA-PSS-BRM1.AccumulatedTotalShiftDose > R1-SGA-PSS-BRM1.AlarmLimitShiftDose2)or(BL-02BM-PSS-BRM1.AccumulatedTotalShiftDose > BL-02BM-PSS-BRM1.AlarmLimitShiftDose2)or(BL-08ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-08ID-PSS-BRM1.AlarmLimitShiftDose2 )) | ALARM/RAD/R1_RAD_PYALARM02 | False | +48 571 240 691 | Tak | Tak | if accul=mulates shift dose is abouve limit, restars every 4 hours (8:00-12:00. 12:00-16:00, 16:00-20:00)
I_DIA_LIBERA_ILK | Interlock notified on any Libera in Linac | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | I | DIA | if (libera I interlock == True) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 511 176 557 | Nie | Tak | Operator fault or magnes malfunction
I_DIA_LIBERA_TEMP | Temperature too high (over 75) in any of LSPE in Linac | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | I | DIA | if (libera I temp > 75) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 511 176 557 | Nie | Tak | Time for Libera cleaning
I_TL_DIA_LIBERA_ILK | Interlock notified on any Libera in TL | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | I | DIA | if (libera TL interlock == True) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 511 176 557 | Nie | Tak | Operator fault or magnes malfunction
I_TL_DIA_LIBERA_TEMP | Temperature too high (over 75) in any of LSPE in TL | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | I | DIA | if (libera TL temp > 75) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 511 176 557 | Nie | Tak | Time for Libera cleaning
R1_DIA_LIBERA_ILK | Interlock notified on any Libera LB+ in R1 | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | R1 | DIA | if( (PLC/R1-ALL/BOOLEAN/B_CALLENDARFLAG_UOD_ACTIVE_S == true) and (R1-01/DIA/R1-01-DIA-BPM1/InterlockXNotified == true or R1-01/DIA/R1-01-DIA-BPM2/InterlockXNotified == true or R1-01/DIA/R1-01-DIA-BPM3/InterlockXNotified == true or R1-02/DIA/R1-02-DIA-BPM1/InterlockXNotified == true or R1-02/DIA/R1-02-DIA-BPM2/InterlockXNotified == true or R1-02/DIA/R1-02-DIA-BPM3/InterlockXNotified == true or R1-03/DIA/R1-03-DIA-BPM1/InterlockXNotified == true or R1-03/DIA/R1-03-DIA-BPM2/InterlockXNotified == true or R1-03/DIA/R1-03-DIA-BPM3/InterlockXNotified == true or R1-04/DIA/R1-04-DIA-BPM1/InterlockXNotified == true or R1-04/DIA/R1-04-DIA-BPM2/InterlockXNotified == true or R1-04/DIA/R1-04-DIA-BPM3/InterlockXNotified == true or R1-05/DIA/R1-05-DIA-BPM1/InterlockXNotified == true or R1-05/DIA/R1-05-DIA-BPM2/InterlockXNotified == true or R1-05/DIA/R1-05-DIA-BPM3/InterlockXNotified == true or R1-06/DIA/R1-06-DIA-BPM1/InterlockXNotified == true or R1-06/DIA/R1-06-DIA-BPM2/InterlockXNotified == true or R1-06/DIA/R1-06-DIA-BPM3/InterlockXNotified == true or R1-07/DIA/R1-07-DIA-BPM1/InterlockXNotified == true or R1-07/DIA/R1-07-DIA-BPM2/InterlockXNotified == true or R1-07/DIA/R1-07-DIA-BPM3/InterlockXNotified == true or R1-08/DIA/R1-08-DIA-BPM1/InterlockXNotified == true or R1-08/DIA/R1-08-DIA-BPM2/InterlockXNotified == true or R1-08/DIA/R1-08-DIA-BPM3/InterlockXNotified == true or R1-09/DIA/R1-09-DIA-BPM1/InterlockXNotified == true or R1-09/DIA/R1-09-DIA-BPM2/InterlockXNotified == true or R1-09/DIA/R1-09-DIA-BPM3/InterlockXNotified == true or R1-10/DIA/R1-10-DIA-BPM1/InterlockXNotified == true or R1-10/DIA/R1-10-DIA-BPM2/InterlockXNotified == true or R1-10/DIA/R1-10-DIA-BPM3/InterlockXNotified == true or R1-11/DIA/R1-11-DIA-BPM1/InterlockXNotified == true or R1-11/DIA/R1-11-DIA-BPM2/InterlockXNotified == true or R1-11/DIA/R1-11-DIA-BPM3/InterlockXNotified == true or R1-12/DIA/R1-12-DIA-BPM1/InterlockXNotified == true or R1-12/DIA/R1-12-DIA-BPM2/InterlockXNotified == true or R1-12/DIA/R1-12-DIA-BPM3/InterlockXNotified == true or R1-01/DIA/R1-01-DIA-BPM1/InterlockZNotified == true or R1-01/DIA/R1-01-DIA-BPM2/InterlockZNotified == true or R1-01/DIA/R1-01-DIA-BPM3/InterlockZNotified == true or R1-02/DIA/R1-02-DIA-BPM1/InterlockZNotified == true or R1-02/DIA/R1-02-DIA-BPM2/InterlockZNotified == true or R1-02/DIA/R1-02-DIA-BPM3/InterlockZNotified == true or R1-03/DIA/R1-03-DIA-BPM1/InterlockZNotified == true or R1-03/DIA/R1-03-DIA-BPM2/InterlockZNotified == true or R1-03/DIA/R1-03-DIA-BPM3/InterlockZNotified == true or R1-04/DIA/R1-04-DIA-BPM1/InterlockZNotified == true or R1-04/DIA/R1-04-DIA-BPM2/InterlockZNotified == true or R1-04/DIA/R1-04-DIA-BPM3/InterlockZNotified == true or R1-05/DIA/R1-05-DIA-BPM1/InterlockZNotified == true or R1-05/DIA/R1-05-DIA-BPM2/InterlockZNotified == true or R1-05/DIA/R1-05-DIA-BPM3/InterlockZNotified == true or R1-06/DIA/R1-06-DIA-BPM1/InterlockZNotified == true or R1-06/DIA/R1-06-DIA-BPM2/InterlockZNotified == true or R1-06/DIA/R1-06-DIA-BPM3/InterlockZNotified == true or R1-07/DIA/R1-07-DIA-BPM1/InterlockZNotified == true or R1-07/DIA/R1-07-DIA-BPM2/InterlockZNotified == true or R1-07/DIA/R1-07-DIA-BPM3/InterlockZNotified == true or R1-08/DIA/R1-08-DIA-BPM1/InterlockZNotified == true or R1-08/DIA/R1-08-DIA-BPM2/InterlockZNotified == true or R1-08/DIA/R1-08-DIA-BPM3/InterlockZNotified == true or R1-09/DIA/R1-09-DIA-BPM1/InterlockZNotified == true or R1-09/DIA/R1-09-DIA-BPM2/InterlockZNotified == true or R1-09/DIA/R1-09-DIA-BPM3/InterlockZNotified == true or R1-10/DIA/R1-10-DIA-BPM1/InterlockZNotified == true or R1-10/DIA/R1-10-DIA-BPM2/InterlockZNotified == true or R1-10/DIA/R1-10-DIA-BPM3/InterlockZNotified == true or R1-11/DIA/R1-11-DIA-BPM1/InterlockZNotified == true or R1-11/DIA/R1-11-DIA-BPM2/InterlockZNotified == true or R1-11/DIA/R1-11-DIA-BPM3/InterlockZNotified == true or R1-12/DIA/R1-12-DIA-BPM1/InterlockZNotified == true or R1-12/DIA/R1-12-DIA-BPM2/InterlockZNotified == true or R1-12/DIA/R1-12-DIA-BPM3/InterlockZNotified == true) ) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Nie | Tak | Beam dump or orbit correction stopped
R1_DIA_LIBERA_PLL | MC PLL unlocked, problem with timing | ALARM | diagnostics.synchrotron@uj.edu.pl | R1 | DIA | if( (PLC/R1-ALL/BOOLEAN/B_CALLENDARFLAG_UOD_ACTIVE_S == true) and (R1-01/DIA/R1-01-DIA-BPM1/ MCPLLStatus == false or R1-01/DIA/R1-01-DIA-BPM2/ MCPLLStatus == false or R1-01/DIA/R1-01-DIA-BPM3/ MCPLLStatus == false or R1-02/DIA/R1-02-DIA-BPM1/ MCPLLStatus == false or R1-02/DIA/R1-02-DIA-BPM2/ MCPLLStatus == false or R1-02/DIA/R1-02-DIA-BPM3/ MCPLLStatus == false or R1-03/DIA/R1-03-DIA-BPM1/ MCPLLStatus == false or R1-03/DIA/R1-03-DIA-BPM2/ MCPLLStatus == false or R1-03/DIA/R1-03-DIA-BPM3/ MCPLLStatus == false or R1-04/DIA/R1-04-DIA-BPM1/ MCPLLStatus == false or R1-04/DIA/R1-04-DIA-BPM2/ MCPLLStatus == false or R1-04/DIA/R1-04-DIA-BPM3/ MCPLLStatus == false or R1-05/DIA/R1-05-DIA-BPM1/ MCPLLStatus == false or R1-05/DIA/R1-05-DIA-BPM2/ MCPLLStatus == false or R1-05/DIA/R1-05-DIA-BPM3/ MCPLLStatus == false or R1-06/DIA/R1-06-DIA-BPM1/ MCPLLStatus == false or R1-06/DIA/R1-06-DIA-BPM2/ MCPLLStatus == false or R1-06/DIA/R1-06-DIA-BPM3/ MCPLLStatus == false or R1-07/DIA/R1-07-DIA-BPM1/ MCPLLStatus == false or R1-07/DIA/R1-07-DIA-BPM2/ MCPLLStatus == false or R1-07/DIA/R1-07-DIA-BPM3/ MCPLLStatus == false or R1-08/DIA/R1-08-DIA-BPM1/ MCPLLStatus == false or R1-08/DIA/R1-08-DIA-BPM2/ MCPLLStatus == false or R1-08/DIA/R1-08-DIA-BPM3/ MCPLLStatus == false or R1-09/DIA/R1-09-DIA-BPM1/ MCPLLStatus == false or R1-09/DIA/R1-09-DIA-BPM2/ MCPLLStatus == false or R1-09/DIA/R1-09-DIA-BPM3/ MCPLLStatus == false or R1-10/DIA/R1-10-DIA-BPM1/ MCPLLStatus == false or R1-10/DIA/R1-10-DIA-BPM2/ MCPLLStatus == false or R1-10/DIA/R1-10-DIA-BPM3/ MCPLLStatus == false or R1-11/DIA/R1-11-DIA-BPM1/ MCPLLStatus == false or R1-11/DIA/R1-11-DIA-BPM2/ MCPLLStatus == false or R1-11/DIA/R1-11-DIA-BPM3/ MCPLLStatus == false or R1-12/DIA/R1-12-DIA-BPM1/ MCPLLStatus == false or R1-12/DIA/R1-12-DIA-BPM2/ MCPLLStatus == false or R1-12/DIA/R1-12-DIA-BPM3/ MCPLLStatus == false )) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Tak | Tak | Too big master oscillator frequency change or phase is not kept during the frequency jump
R1_DIA_LIBERA_PM | Post Mortem notified | WARNING | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | R1 | DIA | if( (PLC/R1-ALL/BOOLEAN/B_CALLENDARFLAG_UOD_ACTIVE_S == true) and (R1-01/DIA/R1-01-DIA-BPM1/ PMNotified == true or R1-01/DIA/R1-01-DIA-BPM2/ PMNotified == true or R1-01/DIA/R1-01-DIA-BPM3/ PMNotified == true or R1-02/DIA/R1-02-DIA-BPM1/ PMNotified == true or R1-02/DIA/R1-02-DIA-BPM2/ PMNotified == true or R1-02/DIA/R1-02-DIA-BPM3/ PMNotified == true or R1-03/DIA/R1-03-DIA-BPM1/ PMNotified == true or R1-03/DIA/R1-03-DIA-BPM2/ PMNotified == true or R1-03/DIA/R1-03-DIA-BPM3/ PMNotified == true or R1-04/DIA/R1-04-DIA-BPM1/ PMNotified == true or R1-04/DIA/R1-04-DIA-BPM2/ PMNotified == true or R1-04/DIA/R1-04-DIA-BPM3/ PMNotified == true or R1-05/DIA/R1-05-DIA-BPM1/ PMNotified == true or R1-05/DIA/R1-05-DIA-BPM2/ PMNotified == true or R1-05/DIA/R1-05-DIA-BPM3/ PMNotified == true or R1-06/DIA/R1-06-DIA-BPM1/ PMNotified == true or R1-06/DIA/R1-06-DIA-BPM2/ PMNotified == true or R1-06/DIA/R1-06-DIA-BPM3/ PMNotified == true or R1-07/DIA/R1-07-DIA-BPM1/ PMNotified == true or R1-07/DIA/R1-07-DIA-BPM2/ PMNotified == true or R1-07/DIA/R1-07-DIA-BPM3/ PMNotified == true or R1-08/DIA/R1-08-DIA-BPM1/ PMNotified == true or R1-08/DIA/R1-08-DIA-BPM2/ PMNotified == true or R1-08/DIA/R1-08-DIA-BPM3/ PMNotified == true or R1-09/DIA/R1-09-DIA-BPM1/ PMNotified == true or R1-09/DIA/R1-09-DIA-BPM2/ PMNotified == true or R1-09/DIA/R1-09-DIA-BPM3/ PMNotified == true or R1-10/DIA/R1-10-DIA-BPM1/ PMNotified == true or R1-10/DIA/R1-10-DIA-BPM2/ PMNotified == true or R1-10/DIA/R1-10-DIA-BPM3/ PMNotified == true or R1-11/DIA/R1-11-DIA-BPM1/ PMNotified == true or R1-11/DIA/R1-11-DIA-BPM2/ PMNotified == true or R1-11/DIA/R1-11-DIA-BPM3/ PMNotified == true or R1-12/DIA/R1-12-DIA-BPM1/ PMNotified == true or R1-12/DIA/R1-12-DIA-BPM2/ PMNotified == true or R1-12/DIA/R1-12-DIA-BPM3/ PMNotified == true )) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Tak | Tak | Please archive the post mortem buffer if future investigation of beam dump cause is required
R1_DIA_LIBERA_CPU_USE | LB+ in R1 CPU usage too high | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | R1 | DIA | if (LB+ CPU >=95) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Nie | Tak | Device server fault or incorrect usage
R1_DIA_LIBERA_TEMP | Temperature too high (over 75) in any of LB+ in R1 | INFO | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | R1 | DIA | if (LB+ temp > 75) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Nie | Tak | Time for Libera cleaning
R1_01S_DIA_SCRP_IN | Scraper in the SR inserted below physical aperture, lifetime measurement or possible beam loss | WARNING | diagnostics.synchrotron@uj.edu.pl | R1 | DIA | if (R1-01S/CTL/R1-01S-CTL-STPMT2/PhysicalPosition < 13.0 or R1-01S/CTL/R1-01S-CTL-STPMT3/PhysicalPosition < 6.5 or R1-01S/CTL/R1-01S-CTL-STPMT4/PhysicalPosition < 6.5) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Nie | Tak | Life time measurement or serious hardware problem
I_TL_DIA_CAM_RUN | Camera is acquirig the signal but YAG is EXTRACTED in TL | WARNING | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | R1 | DIA | if (YAG_X == EXTRACTED and CAM_X.state == RUNNING) - X = 1,…,3 | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Nie | Tak | It is not recommended to leave camera running without purpose in Linac
I_DIA_CAM_RUN | Camera is acquirig the signal but YAG is EXTRACTED in Linac | WARNING | Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | I | DIA | if (YAG_X == EXTRACTED and CAM_X.state == RUNNING) - X = 1,…,7 | ALARM/DIA/I_DIA_PYALARM01 | False | +48 511 176 557 | Nie | Tak | It is not recommended to leave camera running without purpose in Linac
R1_01S_DIA_DCCT_FAIL | Beam current readout failure | WARNING | diagnostics.synchrotron@uj.edu.pl | R1 | DIA | if ((PLC/R1-ALL/BOOLEAN/B_CALLENDARFLAG_UOD_ACTIVE_S == true) and (R1-01S/DIA/R1-01S-DIA-DCCT1/State != ON)) | ALARM/DIA/R1_DIA_PYALARM02 | False | +48 511 176 557 | Tak | Tak | Device server problem
R1_SGDCAB10_CTL_EVG_VIOLATION | Timing, Event Generator violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | R1 | CTL | if (R1-SGD/CTL/R1-SGDCAB10-CTL-EVG/VIOLATION != 0) | ALARM/CTL/R1_CTL_PYALARM02 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
I_K00CAB04_CTL_EVR_VIOLATION | Timing, Event Receiver (I-K00CAB04-CTL-EVR) violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | I | CTL | if (I-K00/CTL/I-K00CAB04-CTL-EVR/VIOLATION != 0) | ALARM/CTL/I_CTL_PYALARM01 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
I_K01CAB04_CTL_EVR_VIOLATION | Timing, Event Receiver (I-K01CAB04-CTL-EVR) violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | I | CTL | if (I-K01/CTL/I-K01CAB04-CTL-EVR/VIOLATION != 0 ) | ALARM/CTL/I_CTL_PYALARM01 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
I_K03CAB04_CTL_EVR_VIOLATION | Timing, Event Receiver (I-K03CAB04-CTL-EVR) violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | I | CTL | if (I-K03/CTL/I-K03CAB04-CTL-EVR/VIOLATION != 0 ) | ALARM/CTL/I_CTL_PYALARM01 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
I_TLCAB01_CTL_EVR_VIOLATION | Timing, Event Receiver (I-TLCAB01-CTL-EVR) violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | I | CTL | if (I-TL/CTL/I-TLCAB01-CTL-EVR/VIOLATION != 0 ) | ALARM/CTL/I_CTL_PYALARM01 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
R1_SGACAB11_CTL_EVR_VIOLATION | Timing, Event Receiver (R1-SGACAB11-CTL-EVR) violation, RAM not initialized or hardware problem | WARNING | diagnostics.synchrotron@uj.edu.pl | R1 | CTL | if (R1-SGA/CTL/R1-SGACAB11-CTL-EVR/VIOLATION != 0 ) | ALARM/CTL/R1_CTL_PYALARM02 | False | +48 511 176 557 | Nie | Tak | If the device is powered on after shutdown, try to clear violations and re-apply RAMs
I_S00_DIA_CHOPPER_OFF | I-K00 is in TRIG mode and Chopper is off | WARNING | Paulina Klimczyk, paulina.klimczyk@uj.edu.pl | I | DIA | if (I_S00_DIA_CHOPPER == 0 and MOD_K00.state == Running) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 519 307 930 | Nie | Tak | Operator fault, beam will be lost in the energy filter
I_S00_DIA_CHOPPER_APT_OUT | Aperture in GUN section is extracted while chopper is ON | WARNING | Paulina Klimczyk, paulina.klimczyk@uj.edu.pl | I | DIA | if (MOT_2 > POS and I_S00_DIA_CHOPPER == 1 ) | ALARM/DIA/I_DIA_PYALARM01 | False | +48 519 307 931 | Nie | Tak | Aperture was nor inserted, chopper is not working efficiently with extracted aperture
I_PSS_BStopper1_2_error | BStopper1 &2 are in unknown state | WARNING | Piotr Gałuszka, piotr.galuszka@uj.edu.pl | I | PSS | if (solaris/pss/0/bstopper1[2] == True or if solaris/pss/0/bstopper2[2] == True) | ALARM/PSS/I_PSS_PYALARM01 | False | 48519307977 | Tak | Tak
R1_PSS_valve1_2_error | Valve1-Ring & Valve2-Ring are in unknown state | WARNING | Piotr Gałuszka, piotr.galuszka@uj.edu.pl | R1 | PSS | if (solaris/pss/0/valve1[2] == True or solaris/pss/0/valve2[2] == True) | ALARM/PSS/R1_PSS_PYALARM02 | False | 48519307977 | Tak | Tak
BL_PSS_injection_disabled | Injection to storage ring disabled by BL04 or BL05 by PSS | INFO | Piotr Gałuszka, piotr.galuszka@uj.edu.pl | BL | PSS | if (solaris/pss/0/bl_04bmpeemxas_injection_enable[6] == False or solaris/pss/0/bl_05iduarpes_injection_enable[6] == False) | ALARM/PSS/R1_PSS_PYALARM02 | False | 48519307977 | Nie | Tak
I_WAT_CHILL_GUN_INTERLOCK | Interlock of water flow for Gun | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if I-K00/WAT/I-K00-WAT-CH/State is not ON or Running | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Water refilling is needed or any problem with water chiller
I_WAT_K00_INTERLOCK | Interlock of water in K00 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-S00-WAT-FSW01 or I-S00-WAT-FSW02 or I-S00-WAT-FSW03 or I-K00-WAT-FSW01 or I-K00-WAT-FSW02 or I-K00-WAT-FSW03 or I-K00-WAT-FGE1) /State is INTERLOCK) | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Problem with flow switch or flow meter or set point adjustment is needed or problem with cooling water pressure
I_WAT_K01_S01_INTERLOCK | Interlock of water in K01 or S01 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-K01/WAT/I-K01-WAT-SHG1 or I-K01-WAT-FSW01 or I-K01-WAT-FSW02 or I-K01-WAT-FSW03 or I-K01-WAT-FGE1 or I-S01A-WAT-FSW01 or I-S01A-WAT-FSW02 or I-S01A-WAT-FSW03 or I-S01A-WAT-FSW04 or I-S01A-WAT-FSW05 or I-S01A-WAT-FSW06 or I-S01A-WAT-FSW07 or I-S01B-WAT-FSW01) /State is INTERLOCK) | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_K02_S02_INTERLOCK | Interlock of water in K02 or S02 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-K02/WAT/I-K02-WAT-SHG1 or I-K02-WAT-FSW01 or I-K02-WAT-FSW02 or I-K02-WAT-FSW03 or I-K02-WAT-FGE1 or I-S02A-WAT-FSW01 or I-S02A-WAT-FSW02 or I-S02A-WAT-FSW03 or I-S02A-WAT-FSW04 or I-S02A-WAT-FSW05 or I-S02A-WAT-FSW06 or I-S02A-WAT-FSW07 or I-S02B-WAT-FSW01) /State is INTERLOCK) | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_K03_S03_INTERLOCK | Interlock of water in K03 or S03 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-K03/WAT/I-K03-WAT-SHG1 or I-K03-WAT-FSW01 or I-K03-WAT-FSW02 or I-K03-WAT-FSW03 or I-K03-WAT-FGE1 or I-S03A-WAT-FSW01 or I-S03A-WAT-FSW02 or I-S03A-WAT-FSW03 or I-S03A-WAT-FSW04 or I-S03A-WAT-FSW05 or I-S03A-WAT-FSW06 or I-S03A-WAT-FSW07 or I-S03B-WAT-FSW01) /State is INTERLOCK) | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_TR_INTERLOCK | Interlock of water in Transfer Line section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-TR1-WAT-FSW01 or I-TR1-WAT-FSW02 or I-TR1-WAT-FSW03 or I-TR1-WAT-FSW04 or I-TR1-WAT-FSW05 or I-TR1-WAT-FSW06 or I-TR1-WAT-FSW07 or I-TR1-WAT-FSW08 or I-TR1-WAT-FSW09 or I-TR1-WAT-FSW010) /State is INTERLOCK) | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_SGD_INTERLOCK | Interlock of water in Service Gallery | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-SHG1 or R1-SGD-WAT-SHG2 or R1-SGD-WAT-SHG3 or R1-SGD-WAT-SHG4 or R1-SGD-WAT-FSW04 or R1-SGD-WAT-FSW05 or R1-SGD-WAT-FSW06 or R1-SGD-WAT-FSW07 or R1-SGD-WAT-FSW08 or R1-SGD-WAT-FSW09 or R1-SGD-WAT-FSW10 or R1-SGD-WAT-FSW11 or R1-SGD-WAT-FSW12 or R1-SGD-WAT-FSW13 or R1-SGD-WAT-FSW14 or R1-SGD-WAT-FGE01 or R1-SGD-WAT-FGE02 or ) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_01_INTERLOCK | Interlock of water in Storage Ring Sector 01 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW01 or R1-01-WAT-FSW01 or R1-01-FSW02 or R1-01-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_02_INTERLOCK | Interlock of water in Storage Ring Sector 02 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW02 or R1-02-WAT-FSW01 or R1-02-FSW02 or R1-02-WAT-FSW03 or R1-02-FSW04 or R1-02-FSW05) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_03_INTERLOCK | Interlock of water in Storage Ring Sector 03 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW03 or R1-03-WAT-FSW01 or R1-03-FSW02 or R1-03-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_04_INTERLOCK | Interlock of water in Storage Ring Sector 04 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW01 or R1-04-WAT-FSW01 or R1-04-FSW02 or R1-04-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_05_INTERLOCK | Interlock of water in Storage Ring Sector 05 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW02 or R1-05-WAT-FSW01 or R1-05-FSW02 or R1-05-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_06_INTERLOCK | Interlock of water in Storage Ring Sector 06 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW03 or R1-06-WAT-FSW01 or R1-06-FSW02 or R1-06-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_07_INTERLOCK | Interlock of water in Storage Ring Sector 07 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW01 or R1-07-WAT-FSW01 or R1-07-FSW02 or R1-07-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_08_INTERLOCK | Interlock of water in Storage Ring Sector 08 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW02 or R1-08-WAT-FSW01 or R1-08-FSW02 or R1-08-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_09_INTERLOCK | Interlock of water in Storage Ring Sector 09 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW03 or R1-09-WAT-FSW01 or R1-09-FSW02 or R1-09-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_10_INTERLOCK | Interlock of water in Storage Ring Sector 10 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW01 or R1-10-WAT-FSW01 or R1-10-FSW02 or R1-10-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_11_INTERLOCK | Interlock of water in Storage Ring Sector 11 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW02 or R1-11-WAT-FSW01 or R1-11-FSW02 or R1-11-WAT-FSW03) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_12_INTERLOCK | Interlock of water in Storage Ring Sector 12 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW03 or R1-12-WAT-FSW01 or R1-12-FSW02 or R1-12-WAT-FSW03 or R1-12-FSW04 or R1-12-FSW05 or R1-12-FSW06 or R1-12-FSW07) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_INTERLOCK | Interlock of water flow for Main Cavity 1 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW01 or R1-12S-WAT-FSW02 or R1-12S-WAT-FSW03 or R1-12S-WAT-FSW04 or R1-12S-WAT-FSW05 or R1-12S-WAT-FSW06 or R1-12S-WAT-FSW07 or R1-12S-WAT-FSW08 or R1-12S-WAT-FSW09) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_INTERLOCK | Interlock of water flow for Main Cavity 2 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW10 or R1-12S-WAT-FSW11 or R1-12S-WAT-FSW12 or R1-12S-WAT-FSW13 or R1-12S-WAT-FSW14 or R1-12S-WAT-FSW15 or R1-12S-WAT-FSW16 or R1-12S-WAT-FSW17 or R1-12S-WAT-FSW18) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV1_INTERLOCK | Interlock of water flow for Landau Cavity 1 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW22 or R1-12S-WAT-FSW23 or R1-12S-WAT-FSW24 ) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV2_INTERLOCK | Interlock of water flow for Landau Cavity 2 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW19 or R1-12S-WAT-FSW20 or R1-12S-WAT-FSW21 ) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_05ID_ALU_CHMBR_INTERLOCK | Interlock of water flow for BL-05ID ALU Chamber | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-04-WAT-FSW04 or R1-04-WAT-FSW05) /State is INTERLOCK) | ALARM/PLC/R1_PLC_PYALARM02 | False | 48519307997 | Tak | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_DIRECT_COUPLER_INTERLOCK | Interlock of water flow for Directional Coupler | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S00-WAT-FSW01 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False |  | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_SOLT1_INTERLOCK | Interlock of water flow for Solenoid 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S00-WAT-FSW02 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False |  | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_CIRC_DUMM_L1_INTERLOCK | Interlock of water flow for Circulator Dummy Load 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K00-WAT-FSW01 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False |  | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_CIRCULATOR_INTERLOCK | Interlock of water flow for Circulator | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K00-WAT-FSW03 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False |  | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_CIRC_RF_WINDOW_INTERLOCK | Interlock of water flow for RF Window | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K00-WAT-FGE1 flow meter | ALARM/PLC/I_PLC_PYALARM01 | False |  | Nie | Tak | Problem with flow meter or problem with cooling water pressure
I_WAT_K01_SHG_INTERLOCK | Interlock of water flow for SHG K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K01-WAT-SHG1 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with SHG
I_WAT_K01_MOD_INTERLOCK | Interlock of water flow for Modulator K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K01-WAT-FSW01 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K01_ACC_STR_A_INTERLOCK | Interlock of water flow for Linac Structure A K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K01-WAT-FSW02 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K01_MOD_RF_W_INTERLOCK | Problem with flow meter or problem with cooling water pressure | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K01-WAT-FGE1 flow meter | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak
I_WAT_S01A_SLED1_1_INTERLOCK | Interlock of water flow for SLED 1 K01 FSW01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW01 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_SLED1_2_INTERLOCK | Interlock of water flow for SLED 1 K01 FSW02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW02 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_SLED1_3_INTERLOCK | Interlock of water flow for SLED 1 K01 FSW03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW03 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_SLED2_4_INTERLOCK | Interlock of water flow for SLED 2 K01 FSW04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW04 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_SLED2_5_INTERLOCK | Interlock of water flow for SLED 2 K01 FSW05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW05 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_SLED2_6_INTERLOCK | Interlock of water flow for SLED 2 K01 FSW06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW06 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01A_WAVEGUIDE_A_INTERLOCK | Interlock of water flow for Waveguide A K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01A-WAT-FSW07 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K02_SHG_INTERLOCK | Interlock of water flow for SHG K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K02-WAT-SHG1 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with SHG
I_WAT_K02_MOD_INTERLOCK | Interlock of water flow for Modulator K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K02-WAT-FSW01 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K02_ACC_STR_A_INTERLOCK | Interlock of water flow for Linac Structure A K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K02-WAT-FSW02 flow switch | ALARM/PLC/I_PLC_PYALARM01 | False | 48519307997 | Nie | Tak | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_RF_LLRF_ARCSA | STOP_OPERATION_SR_Circulator_1_arc_detection_alarm_from_LLRF | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_ArcsA == True) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak | Arcing detected by LLRF in SR circulator 1
R1_RF_PLC_ARCSA | STOP_OPERATION_SR_Circulator_1_arc_detection_alarm_from_PLC | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | CTL | if ((xx_ARCDR1_CHA_A == TRUE) OR (xx_ARCDR1_CHB_A) == TRUE) | ALARM/CTL/R1_CTL_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF_ENDSWITCH_CAV_A | STOP_OPERATION_100MHz_cavity_A_limit_switch_activated | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_EndSwitchUpA == True)) or (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_EndSwitchDownA == True)) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF_ENDSWITCH_LANDAU_A | STOP_OPERATION_Landau_cavity_A_limit_switch_activated | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_PlungerEndSwitchUpA == True)) or (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_PlungerEndSwitchDownA == True)) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak | to check name:Diag_PlungerEndSwitchUp
R1_RF_VAC_ION_PUMP_BYPASS | STOP_OPERATION_bypass_of_any_ion_pumps_for_cavity | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | VAC | if any ((CAB09-IPCU01 to CAB09-IPCU01)/bypass== True)) | ALARM/VAC/R1_VAC_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_RELAY_BOX_CAV_A | 100MHz_cavity_A_Relay_Box_contact_open | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if (relay open == true) [o nazwe tagu pytac KW] | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_RELAY_BOX_LANDAU_A | Landau_cavity_A_Relay_Box_contact_open | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if (relay open == true) [o nazwe tagu pytac KW] | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_PAPCW1_ON_NOT_ENABLED | STOP_OPERATION_transmitter_1_ON_but_ no_ enable_signal_from_PLC | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((R1-SGD/RF/R1-SGD-RF-PAPCW1/AmpON == true) AND (PAPCW1_Q8_Q9_ENABLED_S == false)) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak | Misconfiguration or enable signal detection problem
R1_RF_PAPCW2_ON_NOT_ENABLED | STOP_OPERATION_transmitter_2_ON_but_ no_ enable_signal_from_PLC | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((R1-SGD/RF/R1-SGD-RF-PAPCW2/AmpON == true) AND (PAPCW2_Q8_Q9_ENABLED_S== false)) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak | Misconfiguration or enable signal detection problem
R1_RF_PAPCW1_ON_TUNING_CAV_A | transmitter_1_is_ON_but_cavity_A_tuned_beyond_PLC_ limit | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((R1_12SCAV1_RF_CAVPOT1 <= 4.3) OR (R1_12SCAV1_RF_CAVPOT1 >= 7.9) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_PAPCW1_2_ON_TUNING_LANDAU_A_B | transmitter_1_or_2_is_ON_but_Landau_tuned_beyond_PLC_ limit | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if (((R1_12SCAV1_RF_CAVPOT3 <= 2.8) OR (R1_12SCAV1_RF_CAVPOT3 >= 8.2) OR (R1_12SCAV1_RF_CAVPOT4 <= 2.8) OR (R1_12SCAV1_RF_CAVPOT4 >= 8.2)) AND ((R1-SGD/RF/R1-SGD-RF-PAPCW1/AmpON == true) OR (R1-SGD/RF/R1-SGD-RF-PAPCW2/AmpON == true))) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
I_RF_KLY_BYPASS | any klystron RF drivers in bypass during injection | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | if ((injection==ON) and (any bypass == true)) | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_SHGX_CONDITIONING_MODE | STOP_OPERATION_Injection is active but SHG is in conditioning mode | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | CTL | if ((injection==ON) and ((SHG1==conditioning_mode) or (SHG2==conditioning_mode))) | ALARM/CTL/R1_CTL_PYALARM02 | False | 48519307967 | Tak | Tak | Switch all SHGs into beam mode for beam operation
I_RF_I_K00_INTERNAL_INTERLOCK | I-K00 Modulator internal interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K00-RF-MOD1:: if ((any alarm from K2Interlock.h) and NOT(alarm from K2Interlock.h( {0x1001, "Sys\\HwCtr\\StandBy interlock 1\\Problem with 24V PLC loop"},{0x8005, "Sys\\HwCtr\\Trig interlock 2\\Linac water"}, {0x8004, "Sys\\HwCtr\\Trig interlock 1\\Linac vacuum"}, {0x4002, "Sys\\HwCtr\\Hv interlock 2\\PSS interlock"})) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K01_INTERNAL_INTERLOCK | I-K01 Modulator internal interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K01-RF-MOD1:: if ((any alarm from K2Interlock.h) and NOT(alarm from K2Interlock.h( {0x1001, "Sys\\HwCtr\\StandBy interlock 1\\Problem with 24V PLC loop"},{0x8005, "Sys\\HwCtr\\Trig interlock 2\\Linac water"}, {0x8004, "Sys\\HwCtr\\Trig interlock 1\\Linac vacuum"}, {0x4002, "Sys\\HwCtr\\Hv interlock 2\\PSS interlock"})) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K02_INTERNAL_INTERLOCK | I-K02 Modulator internal interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K02-RF-MOD1:: if ((any alarm from K2Interlock.h) and NOT(alarm from K2Interlock.h( {0x1001, "Sys\\HwCtr\\StandBy interlock 1\\Problem with 24V PLC loop"},{0x8005, "Sys\\HwCtr\\Trig interlock 2\\Linac water"}, {0x8004, "Sys\\HwCtr\\Trig interlock 1\\Linac vacuum"}, {0x4002, "Sys\\HwCtr\\Hv interlock 2\\PSS interlock"})) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K03_INTERNAL_INTERLOCK | I-K03 Modulator internal interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K03-RF-MOD1:: if ((any alarm from K2Interlock.h) and NOT(alarm from K2Interlock.h( {0x1001, "Sys\\HwCtr\\StandBy interlock 1\\Problem with 24V PLC loop"},{0x8005, "Sys\\HwCtr\\Trig interlock 2\\Linac water"}, {0x8004, "Sys\\HwCtr\\Trig interlock 1\\Linac vacuum"}, {0x4002, "Sys\\HwCtr\\Hv interlock 2\\PSS interlock"})) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K00_KLYSTRON_VACUUM_INTERLOCK | STOP_OPERATION_I-K00-klystron_vacuum_interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K00-RF-MOD1:: if I({0x1020, "RF\\Klystron vacuum (RF vacuum 2) from RF node"} or {0x1700, "RF\\Vacuum 1 interlock from PLC"} or {0x8714, "RF\\PLC\\Vacuum 2 interlock"} or {0x4042, "RF\\Cool\\Klystron vacuum (RF vacuum 1)"} ) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K01_KLYSTRON_VACUUM_INTERLOCK | STOP_OPERATION_I-K01-klystron vacuum_interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K01-RF-MOD1:: if I({0x1020, "RF\\Klystron vacuum (RF vacuum 2) from RF node"} or {0x1700, "RF\\Vacuum 1 interlock from PLC"} or {0x8714, "RF\\PLC\\Vacuum 2 interlock"} or {0x4042, "RF\\Cool\\Klystron vacuum (RF vacuum 1)"} ) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K02_KLYSTRON_VACUUM_INTERLOCK | STOP_OPERATION_I-K02-klystron vacuum_interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K02-RF-MOD1:: if I({0x1020, "RF\\Klystron vacuum (RF vacuum 2) from RF node"} or {0x1700, "RF\\Vacuum 1 interlock from PLC"} or {0x8714, "RF\\PLC\\Vacuum 2 interlock"} or {0x4042, "RF\\Cool\\Klystron vacuum (RF vacuum 1)"} ) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K03_KLYSTRON_VACUUM_INTERLOCK | STOP_OPERATION_I-K03-klystron vacuum_interlock (SHOW MESSAGE FROM DS. and SENT VIA SMS!) | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | I-K03-RF-MOD1:: if I({0x1020, "RF\\Klystron vacuum (RF vacuum 2) from RF node"} or {0x1700, "RF\\Vacuum 1 interlock from PLC"} or {0x8714, "RF\\PLC\\Vacuum 2 interlock"} or {0x4042, "RF\\Cool\\Klystron vacuum (RF vacuum 1)"} ) | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K00_KLYSTRON_FILAMENT_INTERLOCK | STOP_OPERATION_I-K00-klystron_filament_interlock | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | if ((I-K00-RF-MOD == TRIG) and (I-K00-RF-MOD1/FilamentCurrent != 10.8)) +/-0.1 | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K01_KLYSTRON_FILAMENT_INTERLOCK | STOP_OPERATION_I-K01-klystron_filament_interlock | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | if ((I-K01-RF-MOD == TRIG) and (I-K00-RF-MOD1/FilamentCurrent != 19)) +/-0.1 | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K02_KLYSTRON_FILAMENT_INTERLOCK | STOP_OPERATION_I-K02-klystron filament_interlock | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | if ((I-K02-RF-MOD == TRIG) and (I-K00-RF-MOD1/FilamentCurrent != 19.6)) +/-0.1 | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
I_RF_I_K03_KLYSTRON_FILAMENT_INTERLOCK | STOP_OPERATION_I-K03-klystron filament_interlock | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | I | RF | if ((I-K03-RF-MOD == TRIG) and (I-K00-RF-MOD1/FilamentCurrent != 18.9)) +/-0.1 | ALARM/RF/I_RF_PYALARM01 | False | 48519307967 | Tak | Tak
R1_RF_LLRF1_EPSITCKDISABLEA | STOP OPERATION LLRF1/EpsItckDisableA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF1/EpsItckDisableA == true | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF1_FIMITCKDISABLEA | STOP OPERATION LLRF1/FimItckDisableA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF1/FimItckDisableA == true | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKRVCAVA | STOP OPERATION LLRF2/DisableItckRvcavA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckRvcavA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKMANUALINTERLOCKA | STOP OPERATION LLRF2/DisableItckManualInterlockA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckManualInterlockA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKARCSA | STOP OPERATION LLRF2/DisableItckArcsA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckArcsA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKVACCUMA | STOP OPERATION DisableItckVaccum | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckVaccumA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKPLUNGERENDSWITCHESUPA | STOP OPERATION LLRF2/DisableItckPlungerEndSwitchesUpA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckPlungerEndSwitchesUpA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LLRF2_DISABLEITCKPLUNGERENDSWITCHESDOWNA | STOP OPERATION LLRF2/DisableItckPlungerEndSwitchesDownA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckPlungerEndSwitchesDownA != 0 | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak
R1_RF_LANDAU3GEVRINGENABLEA | STOP OPERATION Landau3gevRingEnableA | ALARM | Paweł Borowiec, pawel.borowiec@uj.edu.pl | R1 | RF | Landau3gevRingEnableA == true | ALARM/RF/R1_RF_PYALARM02 | False | 48519307967 | Tak | Tak

## Etap_2
tag | description | severity | receivers | System | Podsystem | Opis funkcyjny alarmu: | formula | SMS: | Logbook: | Komentarz:
RAD_BRM02_WAR | Radiation Station number 02G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if((BL-04BM-PSS-BRM1.Gamma Dose Rate or BL-04BM-PSS-BRM1.Total Dose Rate > BL-04BM-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM02_ALARM | Radiation Station number 02G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(BL-04BM-PSS-BRM1.AccumulatedTotalShiftDose > BL-04BM-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM03_WAR | Radiation Station number 03G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if((BL-05ID-PSS-BRM1.Gamma Dose Rate or BL-05ID-PSS-BRM1.Total Dose Rate) > BL-05ID-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM03_ALARM | Radiation Station number 03G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(BL-05ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-05ID-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM04_WAR | Radiation Station number 04G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(( BL-06ID-PSS-BRM1.Gamma Dose Rate or BL-06ID-PSS-BRM1.Total Dose Rate) > BL-06ID-PSS-BRM1.AlarmLimitDoseRate2) |  | 48571240691 | Nie
RAD_BRM04_ALARM | Radiation Station number 04G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(BL-06ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-06ID-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM05_WAR | Radiation Station number 05G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(( R1-01R-PSS-BRM1.Gamma Dose Rate or R1-01R-PSS-BRM1.Total Dose Rate) > R1-01R-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM05_ALARM | Radiation Station number 05G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(R1-01R-PSS-BRM1.AccumulatedTotalShiftDose > R1-01R-PSS-BRM1.AlarmLimitShiftDose2 ) |  | 48571240691 | Tak
RAD_BRM06_WAR | Radiation Station number 06G+N; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if ((BL-01-PSS-BRM1.Gamma Dose Rate or BL-01-PSS-BRM1.Total Dose Rate) > BL-01-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM06_ALARM | Radiation Station number 06G+N; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(BL-01-PSS-BRM1.AccumulatedTotalShiftDose > BL-01-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM07_WAR | Radiation Station number 07G+N; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if ((R1-SGA-PSS-BRM1.Gamma Dose Rate or R1-SGA-PSS-BRM1.Total Dose Rate) > R1-SGA-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM07_ALARM | Radiation Station number 07G+N; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if( R1-SGA-PSS-BRM1.AccumulatedTotalShiftDose > R1-SGA-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM08_WAR | Radiation Station number 08G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if ((BL-02BM-PSS-BRM1.Gamma Dose Rate or BL-02BM-PSS-BRM1.Total Dose Rate) > BL-02BM-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM08_ALARM | Radiation Station number 08G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if (BL-02BM-PSS-BRM1.AccumulatedTotalShiftDose > BL-02BM-PSS-BRM1.AlarmLimitShiftDose2) |  | 48571240691 | Tak
RAD_BRM09_WAR | Radiation Station number 09G; exceeded Total Dose rate- Alarm 2 | WARNING | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if ((BL-08ID-PSS-BRM1.Gamma Dose Rate or BL-08ID-PSS-BRM1.Total Dose Rate) > BL-08ID-PSS-BRM1.AlarmLimitDoseRate2 ) |  | 48571240691 | Nie
RAD_BRM09_ALARM | Radiation Station number 09G; exceeded Accumulated shift dose- Alarm 2 | ALARM | Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl | R1 | PSS | if(BL-08ID-PSS-BRM1.AccumulatedTotalShiftDose > BL-08ID-PSS-BRM1.AlarmLimitShiftDose2 ) |  | 48571240691 | Tak
R1_MAG_CIRCUIT_RES_2 | Dangerous change of circuit resistance - PS2 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,35 * 1,1 ) < Resistance [ R1-C134-MAG-PS2 ] < ( 0,35 * 0,9 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_2_WAR | Dangerous change of circuit resistance - PS2 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,35 * 1,05 ) < Resistance [ R1-C134-MAG-PS2 ] < ( 0,35 * 0,95 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_3 | Dangerous change of circuit resistance - PS3 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,33 * 1,1 ) < Resistance [ R1-C134-MAG-PS3 ] < ( 0,33 * 0,9 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_3_WAR | Dangerous change of circuit resistance - PS3 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,33 * 1,05 ) < Resistance [ R1-C134-MAG-PS3 ] < ( 0,33 * 0,95 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_4 | Dangerous change of circuit resistance - PS4 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,34 * 1,1 ) < Resistance [ R1-C134-MAG-PS4 ] < ( 0,34 * 0,9 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_4_WAR | Dangerous change of circuit resistance - PS4 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,34 * 1,05 ) < Resistance [ R1-C134-MAG-PS4 ] < ( 0,34 * 0,95 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_5 | Dangerous change of circuit resistance - PS5 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,31 * 1,1 ) < Resistance [ R1-C134-MAG-PS5 ] < ( 0,31 * 0,9 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_5_WAR | Dangerous change of circuit resistance - PS5 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,31 * 1,05 ) < Resistance [ R1-C134-MAG-PS5 ] < ( 0,31 * 0,95 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_SI | Dangerous change of circuit resistance - PS19 | ALARM | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,0548 * 1,1 ) < Resistance [ R1-SGBCAB06-MAG-PS19 ] < ( 0,0548 * 0,9 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
R1_MAG_CIRCUIT_RES_SI_WAR | Dangerous change of circuit resistance - PS19 | WARNING | Szymon Piela, szymon.piela@uj.edu.pl | R1 | MAG | if ( ( ( 0,0548 * 1,05 ) < Resistance [ R1-SGBCAB06-MAG-PS19 ] < ( 0,0548 * 0,95 )) and ( t > 10 s ) ) |  | 48519307974 | Nie
I_WAT_SOLT2_INTERLOCK | Interlock of water flow for Solenoid 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S00-WAT-FSW03 flow switch |  |  | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_CIRC_DUMM_L2_INTERLOCK | Interlock of water flow for Circulator Dummy Load 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K00-WAT-FSW02 flow switch |  |  | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K01_ACC_STR_B_INTERLOCK | Interlock of water flow for Linac Structure B K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K01-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S01B_WAVEGUIDE_B_INTERLOCK | Interlock of water flow for Waveguide B K01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S01B-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K02_S02_INTERLOCK | Interlock of water in K02 or S02 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-K02/WAT/I-K02-WAT-SHG1 or I-K02-WAT-FSW01 or I-K02-WAT-FSW02 or I-K02-WAT-FSW03 or I-K02-WAT-FGE1 or I-S02A-WAT-FSW01 or I-S02A-WAT-FSW02 or I-S02A-WAT-FSW03 or I-S02A-WAT-FSW04 or I-S02A-WAT-FSW05 or I-S02A-WAT-FSW06 or I-S02A-WAT-FSW07 or I-S02B-WAT-FSW01) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_K02_ACC_STR_B_INTERLOCK | Interlock of water flow for Linac Structure B K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K02-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K02_MOD_RF_W_INTERLOCK | Interlock of water flow for RF Window of Modulator K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K02-WAT-FGE1 flow meter |  | 48519307997 | Nie | Problem with flow meter or problem with cooling water pressure
I_WAT_S02A_SLED1_1_INTERLOCK | Interlock of water flow for SLED 1 K02 FSW01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_SLED1_2_INTERLOCK | Interlock of water flow for SLED 1 K02 FSW02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_SLED1_3_INTERLOCK | Interlock of water flow for SLED 1 K02 FSW03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_SLED2_4_INTERLOCK | Interlock of water flow for SLED 2 K02 FSW04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_SLED2_5_INTERLOCK | Interlock of water flow for SLED 2 K02 FSW05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_SLED2_6_INTERLOCK | Interlock of water flow for SLED 2 K02 FSW06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02A_WAVEGUIDE_A_INTERLOCK | Interlock of water flow for Waveguide A K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02A-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S02B_WAVEGUIDE_B_INTERLOCK | Interlock of water flow for Waveguide B K02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S02B-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K03_S03_INTERLOCK | Interlock of water in K03 or S03 section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-K03/WAT/I-K03-WAT-SHG1 or I-K03-WAT-FSW01 or I-K03-WAT-FSW02 or I-K03-WAT-FSW03 or I-K03-WAT-FGE1 or I-S03A-WAT-FSW01 or I-S03A-WAT-FSW02 or I-S03A-WAT-FSW03 or I-S03A-WAT-FSW04 or I-S03A-WAT-FSW05 or I-S03A-WAT-FSW06 or I-S03A-WAT-FSW07 or I-S03B-WAT-FSW01) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_K03_SHG_INTERLOCK | Interlock of water flow for SHG K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K03-WAT-SHG1 flow switch |  | 48519307997 | Nie | Problem with SHG
I_WAT_K03_MOD_INTERLOCK | Interlock of water flow for Modulator K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K03-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K03_ACC_STR_A_INTERLOCK | Interlock of water flow for Linac Structure A K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K03-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K03_ACC_STR_B_INTERLOCK | Interlock of water flow for Linac Structure B K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K03-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_K03_MOD_RF_W_INTERLOCK | Interlock of water flow for RF Window of Modulator K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-K03-WAT-FGE1 flow meter |  | 48519307997 | Nie | Problem with flow meter or problem with cooling water pressure
I_WAT_S03A_SLED1_1_INTERLOCK | Interlock of water flow for SLED 1 K03 FSW01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_SLED1_2_INTERLOCK | Interlock of water flow for SLED 1 K03 FSW02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_SLED1_3_INTERLOCK | Interlock of water flow for SLED 1 K03 FSW03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_SLED2_4_INTERLOCK | Interlock of water flow for SLED 2 K03 FSW04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_SLED2_5_INTERLOCK | Interlock of water flow for SLED 2 K03 FSW05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_SLED2_6_INTERLOCK | Interlock of water flow for SLED 2 K03 FSW06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03A_WAVEGUIDE_A_INTERLOCK | Interlock of water flow for Waveguide A K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03A-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_S03B_WAVEGUIDE_B_INTERLOCK | Interlock of water flow for Waveguide B K03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-S03B-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_TR_INTERLOCK | Interlock of water in Transfer Line section | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | if ( (I-TR1-WAT-FSW01 or I-TR1-WAT-FSW02 or I-TR1-WAT-FSW03 or I-TR1-WAT-FSW04 or I-TR1-WAT-FSW05 or I-TR1-WAT-FSW06 or I-TR1-WAT-FSW07 or I-TR1-WAT-FSW08 or I-TR1-WAT-FSW09 or I-TR1-WAT-FSW010) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
I_WAT_MAG_SM1A_INTERLOCK | Interlock of water flow for TR Septum Magnet SM1A | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW09 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_DIE_INTERLOCK | Interlock of water flow for TR Dipol Magnet DIE | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF1_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF2_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF3_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF4_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF4 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF5_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF5 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_QF6_INTERLOCK | Interlock of water flow for TR Quadrupol Magnet QF6 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_DIF_INTERLOCK | Interlock of water flow for TR Dipol Magnet DIF | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW08 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_MAG_SM1B_INTERLOCK | Interlock of water flow for TR Septum Magnet SM1B | INFO | HVAC, hvac.synchrotron@uj.edu.pl | I | WAT | Any interlock inside I-TR1-WAT-FSW10 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
I_WAT_SGD_INTERLOCK | Interlock of water in Service Gallery | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-SHG1 or R1-SGD-WAT-SHG2 or R1-SGD-WAT-SHG3 or R1-SGD-WAT-SHG4 or R1-SGD-WAT-FSW04 or R1-SGD-WAT-FSW05 or R1-SGD-WAT-FSW06 or R1-SGD-WAT-FSW07 or R1-SGD-WAT-FSW08 or R1-SGD-WAT-FSW09 or R1-SGD-WAT-FSW10 or R1-SGD-WAT-FSW11 or R1-SGD-WAT-FSW12 or R1-SGD-WAT-FSW13 or R1-SGD-WAT-FSW14 or R1-SGD-WAT-FGE01 or R1-SGD-WAT-FGE02 or ) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with SHG or problem with flow switch or flow meter or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_CIRC1_DUMM_L_INTERLOCK | Interlock of water flow for Circulator 1 Dummy Load | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_TRNSMTR1_INTERLOCK | Interlock of water flow for Transmitter 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_TRNSMTR2_INTERLOCK | Interlock of water flow for Transmitter 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MOB_DUMM_L_INTERLOCK | Interlock of water flow for Mobile Dummy Load | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW14 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CIRCULATOR1_INTERLOCK | Interlock of water flow for Circulator | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FGE01 flow meter |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CIRC2_DUMM_L_INTERLOCK | Interlock of water flow for Circulator Dummy Load | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW09 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_TRNSMTR3_INTERLOCK | Interlock of water flow for Transmitter 3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW10 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_TRNSMTR4_INTERLOCK | Interlock of water flow for Transmitter 4 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW11 flow meter |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CIRCULATOR2_INTERLOCK | Interlock of water flow for Circulator | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FGE02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_SHG1_INTERLOCK | Interlock of water flow for SHG1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-SHG1 |  | 48519307997 | Tak | Problem with SHG
R1_WAT_SHG2_INTERLOCK | Interlock of water flow for SHG2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-SHG2 |  | 48519307997 | Tak | Problem with SHG
R1_WAT_SHG3_INTERLOCK | Interlock of water flow for SHG3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-SHG3 |  | 48519307997 | Tak | Problem with SHG
R1_WAT_SHG4_INTERLOCK | Interlock of water flow for SHG4 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-SHG4 |  | 48519307997 | Tak | Problem with SHG
R1_WAT_SHG1_MCAV1_INTERLOCK | Interlock of water flow for SHG1 Main Cavity 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_SHG2_MCAV2_INTERLOCK | Interlock of water flow for SHG2 Main Cavity 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW08 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_SHG3_LCAV1_INTERLOCK | Interlock of water flow for SHG3 Landau Cavity 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW12 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_SHG4_LCAV21_INTERLOCK | Interlock of water flow for SHG4 Landau Cavity 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW13 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_01_INTERLOCK | Interlock of water in Storage Ring Sector 01 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW01 or R1-01-WAT-FSW01 or R1-01-FSW02 or R1-01-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_01_INTERLOCK | Interlock of water flow for Achromat 01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGA-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_01_INTERLOCK | Interlock of water flow for NEG Absorber 01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-01-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_01_INTERLOCK | Interlock of water flow for Distributed Absorber 01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-01-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_01_INTERLOCK | Interlock of water flow for Crotch Absorber 01 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-01-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_02_INTERLOCK | Interlock of water in Storage Ring Sector 02 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW02 or R1-02-WAT-FSW01 or R1-02-FSW02 or R1-02-WAT-FSW03 or R1-02-FSW04 or R1-02-FSW05) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_02_INTERLOCK | Interlock of water flow for Achromat 02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGA-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_02_INTERLOCK | Interlock of water flow for NEG Absorber 02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-02-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_02_INTERLOCK | Interlock of water flow for Distributed Absorber 02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-02-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_02_INTERLOCK | Interlock of water flow for Crotch Absorber 02 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-02-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_KICKER1_02_INTERLOCK | Interlock of water flow for Kicker Chamber 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-02-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_KICKER2_02_INTERLOCK | Interlock of water flow for Kicker Chamber 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-02-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_03_INTERLOCK | Interlock of water in Storage Ring Sector 03 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGA-WAT-FSW03 or R1-03-WAT-FSW01 or R1-03-FSW02 or R1-03-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_03_INTERLOCK | Interlock of water flow for Achromat 03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGA-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_03_INTERLOCK | Interlock of water flow for NEG Absorber 03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-03-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_03_INTERLOCK | Interlock of water flow for Distributed Absorber 03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-03-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_03_INTERLOCK | Interlock of water flow for Crotch Absorber 03 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-03-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_04_INTERLOCK | Interlock of water in Storage Ring Sector 04 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW01 or R1-04-WAT-FSW01 or R1-04-FSW02 or R1-04-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_04_INTERLOCK | Interlock of water flow for Achromat 04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGB-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_04_INTERLOCK | Interlock of water flow for NEG Absorber 04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-04-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_04_INTERLOCK | Interlock of water flow for Distributed Absorber 04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-04-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_04_INTERLOCK | Interlock of water flow for Crotch Absorber 04 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-04-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_05_INTERLOCK | Interlock of water in Storage Ring Sector 05 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW02 or R1-05-WAT-FSW01 or R1-05-FSW02 or R1-05-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_05_INTERLOCK | Interlock of water flow for Achromat 05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGB-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_05_INTERLOCK | Interlock of water flow for NEG Absorber 05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-05-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_05_INTERLOCK | Interlock of water flow for Distributed Absorber 05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-05-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_05_INTERLOCK | Interlock of water flow for Crotch Absorber 05 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-05-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_06_INTERLOCK | Interlock of water in Storage Ring Sector 06 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGB-WAT-FSW03 or R1-06-WAT-FSW01 or R1-06-FSW02 or R1-06-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_06_INTERLOCK | Interlock of water flow for Achromat 06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGB-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_06_INTERLOCK | Interlock of water flow for NEG Absorber 06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-06-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_06_INTERLOCK | Interlock of water flow for Distributed Absorber 06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-06-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_06_INTERLOCK | Interlock of water flow for Crotch Absorber 06 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-06-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_07_INTERLOCK | Interlock of water in Storage Ring Sector 07 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW01 or R1-07-WAT-FSW01 or R1-07-FSW02 or R1-07-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_07_INTERLOCK | Interlock of water flow for Achromat 07 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGC-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_07_INTERLOCK | Interlock of water flow for NEG Absorber 07 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-07-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_07_INTERLOCK | Interlock of water flow for Distributed Absorber 07 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-07-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_07_INTERLOCK | Interlock of water flow for Crotch Absorber 07 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-07-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_08_INTERLOCK | Interlock of water in Storage Ring Sector 08 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW02 or R1-08-WAT-FSW01 or R1-08-FSW02 or R1-08-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_08_INTERLOCK | Interlock of water flow for Achromat 08 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGC-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_08_INTERLOCK | Interlock of water flow for NEG Absorber 08 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-08-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_08_INTERLOCK | Interlock of water flow for Distributed Absorber 08 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-08-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_08_INTERLOCK | Interlock of water flow for Crotch Absorber 08 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-08-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_09_INTERLOCK | Interlock of water in Storage Ring Sector 09 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGC-WAT-FSW03 or R1-09-WAT-FSW01 or R1-09-FSW02 or R1-09-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_09_INTERLOCK | Interlock of water flow for Achromat 09 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGC-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_09_INTERLOCK | Interlock of water flow for NEG Absorber 09 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-09-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_09_INTERLOCK | Interlock of water flow for Distributed Absorber 09 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-09-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_09_INTERLOCK | Interlock of water flow for Crotch Absorber 09 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-09-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_10_INTERLOCK | Interlock of water in Storage Ring Sector 10 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW01 or R1-10-WAT-FSW01 or R1-10-FSW02 or R1-10-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_10_INTERLOCK | Interlock of water flow for Achromat 10 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_10_INTERLOCK | Interlock of water flow for NEG Absorber 10 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-10-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_10_INTERLOCK | Interlock of water flow for Distributed Absorber 10 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-10-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_10_INTERLOCK | Interlock of water flow for Crotch Absorber 10 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-10-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_11_INTERLOCK | Interlock of water in Storage Ring Sector 11 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW02 or R1-11-WAT-FSW01 or R1-11-FSW02 or R1-11-WAT-FSW03) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_11_INTERLOCK | Interlock of water flow for Achromat 11 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_11_INTERLOCK | Interlock of water flow for NEG Absorber 11 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_11_INTERLOCK | Interlock of water flow for Distributed Absorber 11 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_11_INTERLOCK | Interlock of water flow for Crotch Absorber 11 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_12_INTERLOCK | Interlock of water in Storage Ring Sector 12 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-SGD-WAT-FSW03 or R1-12-WAT-FSW01 or R1-12-FSW02 or R1-12-WAT-FSW03 or R1-12-FSW04 or R1-12-FSW05 or R1-12-FSW06 or R1-12-FSW07) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_ACHR_12_INTERLOCK | Interlock of water flow for Achromat 12 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-SGD-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_NEG_ABS_12_INTERLOCK | Interlock of water flow for NEG Absorber 12 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_DISTR_ABS_12_INTERLOCK | Interlock of water flow for Distributed Absorber 12 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_CROTCH_ABS_12_INTERLOCK | Interlock of water flow for Crotch Absorber 12 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_RF_CHMBR1_11_INTERLOCK | Interlock of water flow for RF Chamber 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_RF_CHMBR2_11_INTERLOCK | Interlock of water flow for RF Chamber 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_RF_CHMBR3_11_INTERLOCK | Interlock of water flow for RF Chamber 3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_RF_CHMBR4_11_INTERLOCK | Interlock of water flow for RF Chamber 4 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-11-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_INTERLOCK | Interlock of water flow for Main Cavity 1 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW01 or R1-12S-WAT-FSW02 or R1-12S-WAT-FSW03 or R1-12S-WAT-FSW04 or R1-12S-WAT-FSW05 or R1-12S-WAT-FSW06 or R1-12S-WAT-FSW07 or R1-12S-WAT-FSW08 or R1-12S-WAT-FSW09) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_INN_COND_INTERLOCK | Interlock of water flow for Main Cavity 1 Inner Conductor | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW01 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_OUT_COND_INTERLOCK | Interlock of water flow for Main Cavity 1 Outer Conductor | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW02 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_MANTEL1_INTERLOCK | Interlock of water flow for Main Cavity 1 Mantel 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW03 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_MANTEL2_INTERLOCK | Interlock of water flow for Main Cavity 1 Mantel 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_MANTEL3_INTERLOCK | Interlock of water flow for Main Cavity 1 Mantel 3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_TUN_ECAP_INTERLOCK | Interlock of water flow for Main Cavity 1 Tuning Endcap | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW06 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_STAT_ECAP_INTERLOCK | Interlock of water flow for Main Cavity 1 Static Endcap | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW07 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_INN_ROD1_INTERLOCK | Interlock of water flow for Main Cavity 1 Inner Rod 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW08 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV1_INN_ROD2_INTERLOCK | Interlock of water flow for Main Cavity 1 Inner Rod 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW09 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_INTERLOCK | Interlock of water flow for Main Cavity 2 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW10 or R1-12S-WAT-FSW11 or R1-12S-WAT-FSW12 or R1-12S-WAT-FSW13 or R1-12S-WAT-FSW14 or R1-12S-WAT-FSW15 or R1-12S-WAT-FSW16 or R1-12S-WAT-FSW17 or R1-12S-WAT-FSW18) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_INN_COND_INTERLOCK | Interlock of water flow for Main Cavity 2 Inner Conductor | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW10 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_OUT_COND_INTERLOCK | Interlock of water flow for Main Cavity 2 Outer Conductor | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW11 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_MANTEL1_INTERLOCK | Interlock of water flow for Main Cavity 2 Mantel 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW12 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_MANTEL2_INTERLOCK | Interlock of water flow for Main Cavity 2 Mantel 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW13 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_MANTEL3_INTERLOCK | Interlock of water flow for Main Cavity 2 Mantel 3 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW14 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_TUN_ECAP_INTERLOCK | Interlock of water flow for Main Cavity 2 Tuning Endcap | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW15 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_STAT_ECAP_INTERLOCK | Interlock of water flow for Main Cavity 2 Static Endcap | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW16 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_INN_ROD1_INTERLOCK | Interlock of water flow for Main Cavity 2 Inner Rod 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW17 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_MCAV2_INN_ROD2_INTERLOCK | Interlock of water flow for Main Cavity 2 Inner Rod 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW18 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV1_INTERLOCK | Interlock of water flow for Landau Cavity 1 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW22 or R1-12S-WAT-FSW23 or R1-12S-WAT-FSW24 ) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV1_CENTR_ROD1_INTERLOCK | Interlock of water flow for Landau Cavity 1 Central Rod 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW22 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV1_CENTR_ROD2_INTERLOCK | Interlock of water flow for Landau Cavity 1 Central Rod 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW23 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV1_MANTEL_INTERLOCK | Interlock of water flow for Landau Cavity 1 Mantel | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW24 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV2_INTERLOCK | Interlock of water flow for Landau Cavity 2 | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-12S-WAT-FSW19 or R1-12S-WAT-FSW20 or R1-12S-WAT-FSW21 ) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV2_CENTR_ROD1_INTERLOCK | Interlock of water flow for Landau Cavity 2 Central Rod 1 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW19 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV2_CENTR_ROD2_INTERLOCK | Interlock of water flow for Landau Cavity 2 Central Rod 2 | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW20 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_LCAV2_MANTEL_INTERLOCK | Interlock of water flow for Landau Cavity 2 Mantel | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-12S-WAT-FSW21 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_05ID_ALU_CHMBR_INTERLOCK | Interlock of water flow for BL-05ID ALU Chamber | ALARM | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | if ( (R1-04-WAT-FSW04 or R1-04-WAT-FSW05) /State is INTERLOCK) |  | 48519307997 | Tak | Problem with flow switch or setpoint adjustment is needed or problem with cooling water pressure
R1_WAT_05ID_ALU_CHMBR1_INTERLOCK | Interlock of water flow for ALU Chamber | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-04-WAT-FSW04 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_WAT_05ID_ALU_CHMBR2_INTERLOCK | Interlock of water flow for ALU Chamber | INFO | HVAC, hvac.synchrotron@uj.edu.pl | R1 | WAT | Any interlock inside R1-04-WAT-FSW05 flow switch |  | 48519307997 | Nie | Problem with flow switch or set point adjustment is needed or problem with cooling water pressure
R1_RF_ LLRF1_EpsItckDisableB | STOP OPERATION LLRF1/EpsItckDisableB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF1/EpsItckDisableB == true |  | 48519307967 | Tak
R1_RF_ LLRF1_FimItckDisableB | STOP OPERATION LLRF1/FimItckDisableB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF1/FimItckDisableB == true |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckRvcavB | STOP OPERATION LLRF2/DisableItckRvcavB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckRvcavB != 0 |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckManualInterlockB | STOP OPERATION LLRF2/DisableItckManualInterlockB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckManualInterlockB != 0 |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckArcsB | STOP OPERATION LLRF2/DisableItckArcsB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckArcsB != 0 |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckVaccumB | STOP OPERATION LLRF2/DisableItckVaccumB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckVaccumB != 0 |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckPlungerEndSwitchesUpB | STOP OPERATION LLRF2/DisableItckPlungerEndSwitchesUpB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckPlungerEndSwitchesUpB != 0 |  | 48519307967 | Tak
R1_RF_ LLRF2_DisableItckPlungerEndSwitchesDownB | STOP OPERATION LLRF2/DisableItckPlungerEndSwitchesDownB | ALARM |  | R1 | RF | R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/DisableItckPlungerEndSwitchesDownB != 0 |  | 48519307967 | Tak
R1_RF_ Landau3gevRingEnableB | STOP OPERATION Landau3gevRingEnableB | ALARM |  | R1 | RF | Landau3gevRingEnableB == true |  | 48519307967 | Tak
R1_RF_LLRF_ArcsB | STOP_OPERATION_SR_Circulator_2_arc_detection_alarm_from_LLRF | ALARM |  | R1 | RF | if (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_ArcsB == True) |  | 48519307967 | Tak | Arcing detected by LLRF in SR circulator 2
R1_RF_PLC_ArcsB | STOP_OPERATION_SR_Circulator_2_arc_detection_alarm_from_PLC | ALARM |  | R1 | CTL | if ((xx_ARCDR2_CHA_A == TRUE) OR (xx_ARCDR2_CHB_A) == TRUE) |  | 48519307967 | Tak
R1_RF_LLRF_EndSwitch_Cav_B | STOP_OPERATION_100MHz_cavity_B_limit_switch_activated | ALARM |  | R1 | RF | if ((R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_EndSwitchUpB == True)) or (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_EndSwitchDownB == True)) |  | 48519307967 | Tak
R1_RF_LLRF_EndSwitch_Landau_B | STOP_OPERATION_Landau_cavity_B_limit_switch_activated | ALARM |  | R1 | RF | if ((R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/Diag_EndSwitchUpB == True)) or (R1-SGD/RF/R1-SGDCAB10-RF-LLRF2/ Diag_PlungerEndSwitchDownB == True)) |  | 48519307967 | Tak
R1_RF_Relay_Box_Cav_B | 100MHz_cavity_B_Relay_Box_contact_open | ALARM |  | R1 | RF | if (relay open == true) [o nazwe tagu pytac KW] |  | 48519307967 | Tak
R1_RF_Relay_Box_Landau_B | Landau_cavity_B_Relay_Box_contact_open | ALARM |  | R1 | RF | if (relay open == true) [o nazwe tagu pytac KW] |  | 48519307967 | Tak
R1_RF_PAPCW2_ON_tuning_Cav_B | transmitter_1_is_ON_but_cavity_B_tuned_beyond_PLC_ limit | ALARM |  | R1 | RF | if ((R1_12SCAV1_RF_CAVPOT2 <= 3.7) OR (R1_12SCAV1_RF_CAVPOT2 >= 8.1) |  | 48519307967 | Tak
| any RF device server doesn't work | ALARM | [5 empty] | 48519307967 | Tak
| była wiązka i transmitter załączony i w ciagu 5 sekund nie ma wiazki i transmitter wyłączony | ALARM |  | r1 | DIA |  |  | 48519307967 | Tak
| STOP_OPERATION_low_SF6_pressure_interlock | ALARM |  |  |  | PLC: SF6 == true |  | 48519307967 | Tak
| high glycol temperature in PAPCW1 | WARNING |  | R1 | RF | LiquidOutTemperature>=55 |  | 48519307967 | Tak
| high glycol temperature in PAPCW2 | WARNING |  | R1 | RF | LiquidOutTemperature>=55 |  | 48519307967 | Tak
| low glycol pressure in PAPCW1 | WARNING |  | R1 | RF | CoolantPressure<=1 |  | 48519307967 | Tak
| low glycol pressure in PAPCW2 | WARNING |  | R1 | RF | CoolantPressure<=1 |  | 48519307967 | Tak
R1_RF_TCU6_CAV_A_not_ready | Controller_TCU6_for_Circulator_A_not_ready | INFO |  | R1 | RF | if ((TCU1_COIL_A == true) OR (TCU1_TINH_A == true) OR (TCU1_TAMBL_A == true) OR (TCU1_TINL_A == true) OR (TCU1_T_A == true) OR (TCU1_OK_S == false))
R1_RF_TCU6_CAV_B_not_ready | Controller_TCU6_for_Circulator_B_not_ready | INFO |  | R1 | RF | if ((TCU2_COIL_A == true) OR (TCU2_TINH_A == true) OR (TCU2_TAMBL_A == true) OR (TCU2_TINL_A == true) OR (TCU2_T_A == true) OR (TCU2_OK_S == false))
| injection_ON_but_SR_master oscillator OFF | INFO |  | R1 | RF | if ((injection==ON) and (R1-SGDCAB10-RF-SIG1/RFOUTPUT == false))
| injection_ON_but_LINAC_master oscillator OFF | INFO |  | R1 | RF | if ((injection==ON) and (I-K00CAB03-RF-SIG1/RFOUTPUT == false))
R1_RF_LLRF_interlocked_for_injection | Injection is active but alarm in LLRF is present | INFO |  | R1 | RF | if ((injection==ON) and (any alarm in R1-SGD/RF/R1-SGDCAB10-RF-LLRF2 == True))
| Injection is active but transmitters not ON | INFO |  | R1 | RF
| Injection is active but transmitters not enabled from PLC | INFO |  | R1 | RF
| Injection is active but not confirmed from PSS | INFO |  | R1 | PSS
| Injection is active but modulators not in TRIG | INFO |  | I | RF
| Injection is active but PA chopper not enabled | INFO |  | I | RF
| Injection is active but negative HV chopper not set | INFO |  | I | RF | voltage < 300
| Injection is active but positive HV chopper not set | INFO |  | I | RF | voltage < 300
| Injection is active but chopper exciter RF input 2 not selected | INFO |  | I | RF
| Injection is active but chopper exciter output not enabled | INFO |  | I | RF
| Injection is active but klystron RF drivers not enabled | INFO |  | I | RF
| Injection is active but gun's cathode current <= 3.5V | INFO |  | i | MAG
| increased pressure in any cavity | INFO |  | r1 | vac | if any ((CAB09-IPCU01 to CAB09-IPCU01)/PRESSURE >= 8e-8))
| Modulator not in TRIG but automatic conditioning is active | INFO |  | r1 | RF
| low SF6 pressure | WARNING |  |  |  | SF6 pressure <= 2.5 |  | 48519307967 | Tak
| injection_ON_but_3GHz_drive_line_RF_amplifier_OFF | info |  |  |  | PLC: ??? == false

## Ustawienia
Zespół Solaris: | Subsystem code | Description | System Code | Description | Nr tel. | Ważność: | Logbook: | Station | Code:
Adriana Wawrzyniak, adriana.wawrzyniak@uj.edu.pl | CTL | Control system | I | Injector | +48 504 778 793 | INFO | Tak | S01 G: | BL-02ID-PSS-BRM1
Agata Chrześcijanek, agata.chrzescijanek@uj.edu.pl | DIA | Diagnostic | R1 | Storage ring | +48 504 778 823 | WARNING | Nie | S02 G | BL-04BM-PSS-BRM1
Agnieszka Jelonek, agnieszka.jelonek@uj.edu.pl | ID | Insertion Devices | BL | Beam line | +48 504 996 659 | ALARM |  | S03 G | BL-05ID-PSS-BRM1
Alicja Górkiewicz, alicja.gorkiewicz@uj.edu.pl | LAS | Laser | S | Structure (building) | +48 507 006 582 | ERROR |  | S04 G | BL-06ID-PSS-BRM1
Andrzej Marendziak, andrzej.marendziak@uj.edu.pl | MAG | Magnets | G | Isolated system not connected to other | +48 507 278 072 | CONTROL |  | S05 G | R1-01R-PSS-BRM1
Arkadiusz Kisiel, arkadiusz.kisiel@uj.edu.pl | MEC | Mechanical components | C | Common objectes not related to particular machine system | +48 510 091 744 | DEBUG |  | S06 G+N | BL-01-PSS-BRM1
Emilia Król, emilia.krol@uj.edu.pl | NET | Network | Multi (->Komentarz) |  | +48 510 093 018 |  |  | S07 G+N | R1-SGA-PSS-BRM1
Ewa Musiał, mail@synchrotron.pl | OPT | Optics |  |  | +48 511 176 557 |  |  | S08 G | BL-02BM-PSS-BRM1
Ewa Partyka-Jankowska, ewa.partyka-jankowska@uj.edu.pl | PSS | Personal Safety System |  |  | +48 517 054 296 |  |  | S09 G | BL-08ID-PSS-BRM1
Grzegorz Cioś, grzegorz.cios@uj.edu.pl | RF | RF system |  |  | +48 517 136 267
Grzegorz Kowalski, g.kowalski@uj.edu.pl | VAC | Vacuum |  |  | +48 519 078 081
Ireneusz Zadworny, ireneusz.zadworny@uj.edu.pl | WAT | Water system |  |  | +48 519 078 083
Jacek Kołodziej, jj.kolodziej@uj.edu.pl | EL | Electrical system |  |  | +48 519 078 084
Jacek Szade, jacek.szade@uj.edu.pl | AIR | Pressurized air system |  |  | +48 519 078 087
Katarzyna Bester-Ostrowska, katarzyna.bester-ostrowska@uj.edu.pl | HOT | Following MAX-IV, the heating subsystem |  |  | +48 519 307 867
Katarzyna Tokarz, k.tokarz@uj.edu.pl | HVAC | Building water and cooling system |  |  | +48 519 307 868
Konrad Kubal, konrad.kubal@uj.edu.pl | BMS | Building management system |  |  | +48 519 307 869
Krystian Kędroń, krystian.kedron@uj.edu.pl | Multi (->Komentarz) |  |  |  | +48 519 307 930
Krzysztof Królas, krzysztof.krolas@uj.edu.pl |  |  |  |  | +48 519 307 949
Krzysztof Wawrzyniak, krzysztof.wawrzyniak@uj.edu.pl |  |  |  |  | +48 519 307 950
Leszek Kapłoniak, leszek.kaploniak@uj.edu.pl |  |  |  |  | +48 519 307 964
Łukasz Szabat, lukasz.szabat@uj.edu.pl |  |  |  |  | +48 519 307 965
Magdalena Jaglarz, magdalena.jaglarz@uj.edu.pl |  |  |  |  | +48 519 307 966
Magdalena Janiga, magdalena.janiga@uj.edu.pl |  |  |  |  | +48 519 307 967
Magdalena Szczepanik-Ciba, magdalena.szczepanik-ciba@uj.edu.pl |  |  |  |  | +48 519 307 968
Marcin Knafel, marcin.knafel@uj.edu.pl |  |  |  |  | +48 519 307 970
Marcin Moras, marcin.moras@uj.edu.pl |  |  |  |  | +48 519 307 973
Marcin Nowak, marcin.p.nowak@uj.edu.pl |  |  |  |  | +48 519 307 974
Marcin Rozwadowski, marcin.rozwadowski@uj.edu.pl |  |  |  |  | +48 519 307 975
Marcin Zając, mar.zajac@uj.edu.pl |  |  |  |  | +48 519 307 976
Marek Madura, marek.madura@uj.edu.pl |  |  |  |  | +48 519 307 977
Marek Stankiewicz, m.j.stankiewicz@uj.edu.pl |  |  |  |  | +48 519 307 990
Mateusz Boruchowski, mateusz.boruchowski@uj.edu.pl |  |  |  |  | +48 519 307 997
Mateusz Wojtaszek, mateusz.wojtaszek@uj.edu.pl |  |  |  |  | +48 519 307 998
Michał Fałowski, michal.falowski@uj.edu.pl |  |  |  |  | +48 519 307 999
Michał Gajda, m.gajda@uj.edu.pl |  |  |  |  | +48 519 329 127
Michał Młynarczyk, michal.mlynarczyk@uj.edu.pl |  |  |  |  | +48 519 353 299
Michał Ostoja-Gajewski, michal.ostoja-gajewski@uj.edu.pl |  |  |  |  | +48 519 516 481
Michał Piekarski, michal.piekarski@uj.edu.pl |  |  |  |  | +48 519 537 887
Mirosław Burzyński, miroslaw.burzynski@uj.edu.pl |  |  |  |  | +48 571 240 691
Natalia Olszowska, natalia.olszowska@uj.edu.pl |  |  |  |  | +48 571 445 044
Paulina Klimczyk, paulina.klimczyk@uj.edu.pl |  |  |  |  | +48 571 445 045
Paweł Borowiec, pawel.borowiec@uj.edu.pl |  |  |  |  | +48 690 492 654
Paweł Bulira, pawel.bulira@uj.edu.pl |  |  |  |  | +48 734 137 016
Paweł Czernecki, pawel.czernecki@uj.edu.pl |  |  |  |  | +48 789 070 378
Paweł Furgał, pawel.furgal@uj.edu.pl
Paweł Gębala, pawel.gebala@uj.edu.pl
Paweł Klimecki, pawel.klimecki@uj.edu.pl
Piotr Gałuszka, piotr.galuszka@uj.edu.pl
Piotr Kurdziel, p.kurdziel@uj.edu.pl
Przemysław Peterman, przemyslaw.peterman@uj.edu.pl
Przemysław Sagało, przemyslaw.sagalo@uj.edu.pl
Stanisław Cabała, stanislaw.cabala@uj.edu.pl
Stanisław Witkowski, stanislaw.witkowski@uj.edu.pl
Szymon Piela, szymon.piela@uj.edu.pl
Tadeusz Szymocha, tadeusz.szymocha@uj.edu.pl
Tomasz Sobol, t.sobol@uj.edu.pl
Tomasz Zbylut, tomasz.zbylut@uj.edu.pl
Wojciech Kitka, wojciech.kitka@uj.edu.pl
Wojciech Soroka, wojciech.soroka@uj.edu.pl
diagnostics.synchrotron@uj.edu.pl